## About (ReadMe)
| Date Checked | Checked By | Job Number | By | Start Date | Calc No
|  |  | 157290 | REDACTED | 26 August 2024
| Project |  |  | Subject
| Southern Water - WFL |  |  | Data Summary Request by REDACTED on 23 Aug 2024
About This Calculation:
Author or Custodian | REDACTED
Version | 1
Version Date | 26 August 2024
Purpose | Tabulate Average, Maximum, Minimum, 95th Percentile and Count for all Analytes in the Database Snapshot table for the Peel Common Effluent and UVAOP Effluent associated with Pilot Study
General Approach | 1. REDACTED developed Python Script to obtain the relevant Statics from Database snapshot table 2. The analytes were grouped by category and the data was formatted
General Instructions For Use
References or Resources | Database Snapshot Table - As of 2 July 2024

## Biological Indicator
| Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
| Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit
Clostridia | #/100mL | 800 | 800 | 800 | 800 | 1 | ND | 1 | 0.0185 | 0 | 108
E. coli | #/100mL | 1900 | 3000 | 2450 | 2940 | 2 | ND | 0 | 0 | 0 | 9
Enterococci | #/100mL | 76 | 8900 | 2340 | 7420 | 9 | ND | 0 | 0 | 0 | 3
F+ coliphage | #/100mL | ND | 7 | 2.08 | 5.8 | 13 | ND | 0 | 0 | 0 | 97
Fecal coliform | #/100mL | 6200 | 14000 | 10100 | 13600 | 2 | ND | 0 | 0 | 0 | 63
Non lactose fermenting bacteria | #/100mL | [5 empty] | ND | 0 | 0 | 0 | 1
Non-Coliform Colonies | #/100mL | [5 empty] | ND | 0 | 0 | 0 | 1
Pseudomonas Aeruginosa (Confirmed) | #/100mL | [5 empty] | ND | 46 | 5.75 | 29.9 | 8
Pseudomonas Species (Confirmed) | #/100mL
Total coliform | #/100mL | 7100 | 37000 | 22000 | 35500 | 2 | ND | 0 | 0 | 0 | 111
Cryptosporidium | #/10L | [5 empty] | ND | 0 | 0 | 0 | 8
Giardia | #/10L | [5 empty] | ND | 0 | 0 | 0 | 8
Total Legionella | #/L | [5 empty] | ND | 0 | 0 | 0 | 12
F+ coliphage | #/mL
Somatic coliphage | #/mL | 1 | 5 | 1.8 | 4.2 | 5 | ND | 1 | 0.111 | 0.6 | 9
Total viable count (2 day at 37c) | #/mL | [5 empty] | ND | 69 | 7.48 | 33.2 | 99
Total viable count (3 day at 22c) | #/mL | [5 empty] | ND | 285 | 94.9 | 232 | 76
Total Legionella | cfu | [5 empty] | ND | 0 | 0 | 0 | 3

## Disinfection Byproduct
| Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
| Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit
4-Chloro-m-cresol | ug/L
Bromate | ug/L | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 54
Bromoacetic acid | ug/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Bromochloroacetic acid | ug/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Bromodichloromethane | ug/L | ND | 0 | 0 | 0 | 9 | ND | 0.5 | 0.0393 | 0.372 | 60
Bromoform | ug/L | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 60
Chloroacetic acid | ug/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Chlorodibromomethane | ug/L | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 66
Chloroform | ug/L | ND | 0 | 0 | 0 | 9 | ND | 0.78 | 0.0266 | 0.0345 | 38
Dibromoacetic acid | ug/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Dibromochloroacetic acid | ug/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Dichloroacetic acid | ug/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Dichlorobromoacetic acid | ug/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Dichloromethane | ug/L | ND | 0 | 0 | 0 | 9 | ND | 1.33 | 0.0333 | 0 | 40
Haloacetic acid | ug/L | ND | 0 | 0 | 0 | 5
PNAHs | ug/L | ND | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5
Sum of 9 HAAS | ug/L | ND | 0 | 0 | 0 | 5
Total Trihalomethanes | ug/L | [5 empty] | 0 | 1.85 | 0.265 | 0.99 | 60
Tribromoacetic | ug/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Trichloroacetic acid | ug/L | ND | 1.93 | 0.496 | 1.71 | 10 | ND | 0 | 0 | 0 | 12

## General Water Quality
| Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
| Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit
UV transmittance | % | 0.277 | 44.2 | 23.8 | 37.4 | 12 | 97.4 | 100 | 99.6 | 100 | 117
Temperature | Celsius
|  | 2.9 | 12 | 8.45 | 12 | 17 | 6 | 21.8 | 13.4 | 18.3 | 79
Turbidity | NTU | 0.815 | 56.3 | 3.79 | 7.25 | 145 | ND | 0.629 | 0.0511 | 0.252 | 118
Salinity | PSS
Absorbance at 254nm | cm-1 | 1.91 | 51 | 18.5 | 30 | 133
Redox potential | mV
|  | 6.88 | 262 | 205 | 260 | 7
Biochemical oxygen demand | mg/L | ND | 83.1 | 6.38 | 14 | 141
Chemical oxygen demand | mg/L | 11.7 | 254 | 41.5 | 63.7 | 146 | ND | 25 | 1.32 | 13 | 115
Dissolved organic carbon | mg/L | 6.76 | 25.2 | 10.1 | 13.2 | 144 | ND | 4.81 | 0.0776 | 0.06 | 117
FOG | mg/L
Filtered Chemical oxygen demand | mg/L
Filtered Sample BOD | mg/L
Non-Volatile suspended solids | mg/L | ND | 7.95 | 0.0548 | 0 | 145
Total dissolved solids | mg/L | 469 | 1710 | 746 | 1030 | 146 | ND | 123 | 21.5 | 75.8 | 116
Total organic carbon | mg/L | 6.54 | 70.6 | 11.3 | 16.5 | 143 | ND | 4.55 | 0.083 | 0.4 | 116
Total suspended solids | mg/L | ND | 108 | 11.3 | 25.9 | 145 | ND | 0 | 0 | 0 | 14
Volatile Suspended Solids | mg/L
Color, filtered | mg/L Pt/Co | [5 empty] | ND | 0 | 0 | 0 | 106
Alkalinity, bicarbonate | mg/L as CaCO3 | 119 | 370 | 264 | 322 | 135 | ND | 22.4 | 1.34 | 18.6 | 105
Alkalinity, carbonate | mg/L as CaCO3 | ND | 0 | 0 | 0 | 135 | ND | 0 | 0 | 0 | 8
Alkalinity, total | mg/L as CaCO3 | 119 | 370 | 262 | 319 | 146 | ND | 22.4 | 1.26 | 18.4 | 112
Hardness | mg/L as CaCO3
Chlorine, free | mg/L as Cl2
[7 empty] | ND | 0.06 | 0.01 | 0.045 | 6
Chlorine, total | mg/L as Cl2
[7 empty] | ND | 0.19 | 0.0317 | 0.143 | 6
Toxic Equivalents Lower Bound | pg/L
Toxic Equivalents Upper Bound | pg/L
pH | s.u. | 7.15 | 8.18 | 7.68 | 7.99 | 153
|  | 7.23 | 7.91 | 7.62 | 7.88 | 77
Conductivity | uS/cm

## Inorganic
| Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
| Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit
Ammonia, un-ionized | mg/L
Chloride | mg/L | 101 | 669 | 206 | 344 | 74 | 1.9 | 44.8 | 13.5 | 31.7 | 60
Cyanide Lower Bound | mg/L
Fluoride | mg/L | ND | 0 | 0 | 0 | 72 | ND | 0.06 | 0.00357 | 0.0425 | 56
Fluoride_dissolved | mg/L
Perchlorate (Dissolved) | mg/L | [5 empty] | ND | 0 | 0 | 0 | 8
Silica | mg/L | 1.08 | 16.3 | 10.5 | 13.9 | 12 | 0.09 | 0.92 | 0.289 | 0.664 | 35
Silica, dissolved | mg/L | 2.1 | 14.3 | 10.2 | 11.2 | 60 | 0.15 | 1.03 | 0.501 | 0.997 | 22
Sulfate | mg/L | 43.8 | 125 | 66.6 | 90.8 | 17 | ND | 5.65 | 1.07 | 3.41 | 57
Sulfate, Soluble | mg/L | 53.4 | 86.7 | 65.3 | 81.3 | 12
Sulfide | mg/L | ND | 0.112 | 0.00848 | 0.0419 | 72 | ND | 0.03 | 0.00174 | 0.0115 | 58
Ammonia | mg/L as N | 1.69 | 1.8 | 1.75 | 1.79 | 2 | ND | 1.07 | 0.19 | 0.562 | 93
NH3 plus NH4 | mg/L as N | [5 empty] | 0.0745 | 0.76 | 0.51 | 0.725 | 14
Nitrate | mg/L as N | 2.72 | 4.83 | 3.78 | 4.72 | 2 | ND | 1.2 | 0.0858 | 0.74 | 130
Nitrite | mg/L as N | 0.577 | 0.695 | 0.636 | 0.689 | 2 | ND | 0.0588 | 0.00959 | 0.0231 | 112
Total kjeldahl nitrogen | mg/L as N | ND | 28.9 | 2.44 | 6.83 | 144 | ND | 1.23 | 0.0197 | 0 | 118
Total nitrogen | mg/L as N
Total oxidized nitrogen | mg/L as N
Orthophosphate | mg/L as P | 0.026 | 7.98 | 2.58 | 6.14 | 152 | ND | 0.291 | 0.0447 | 0.145 | 114
Phosphate, total | mg/L as P | [5 empty] | ND | 0.249 | 0.0299 | 0.116 | 99
Phosphorus, total | mg/L as P | 0.319 | 22.3 | 3.28 | 6.84 | 153 | ND | 0.107 | 0.0468 | 0.106 | 16
Bromide | ug/L | 202 | 1290 | 641 | 1230 | 15 | ND | 94.3 | 26.7 | 72.7 | 46
Bromine | ug/L
Chlorate | ug/L | [5 empty] | ND | 0 | 0 | 0 | 58
Chlorite | ug/L | [5 empty] | ND | 8.8 | 0.16 | 0 | 55
Cyanide, free | ug/L | ND | 3.78 | 0.06 | 0 | 63 | ND | 0 | 0 | 0 | 59
Cyanide, total | ug/L | ND | 0 | 0 | 0 | 11

## Metal
| Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
| Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit
Chromium iii, dissolved | mg/L
Chromium vi, dissolved | mg/L
Aluminum | ug/L | ND | 70.5 | 21.3 | 35.6 | 72 | ND | 0 | 0 | 0 | 61
Antimony | ug/L | ND | 0 | 0 | 0 | 6 | ND | 0 | 0 | 0 | 19
Arsenic | ug/L | ND | 1.2 | 0.762 | 1.1 | 72 | ND | 0 | 0 | 0 | 59
Barium | ug/L | 10.5 | 36.3 | 16.4 | 20.6 | 71 | ND | 1.45 | 0.229 | 1.21 | 57
Beryllium | ug/L | ND | 0 | 0 | 0 | 6 | ND | 0 | 0 | 0 | 19
Boron | ug/L | 42 | 158 | 68.4 | 102 | 71 | ND | 68.1 | 23.4 | 51.7 | 55
Cadmium | ug/L | [5 empty] | ND | 0 | 0 | 0 | 12
Cadmium, dissolved | ug/L
Calcium | ug/L | 78900 | 207000 | 108000 | 128000 | 71 | ND | 10400 | 2610 | 7130 | 52
Chromium | ug/L | ND | 1.02 | 0.146 | 0.714 | 7 | ND | 0 | 0 | 0 | 19
Chromium, dissolved | ug/L
Cobalt | ug/L | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 19
Cobalt_dissolved | ug/L
Copper | ug/L | ND | 12.1 | 4.3 | 11.2 | 7 | 0.5 | 18.2 | 8.9 | 17.8 | 4
Copper_dissolved | ug/L
Iron | ug/L | 56.2 | 508 | 108 | 181 | 72 | ND | 0 | 0 | 0 | 61
Iron, dissolved | ug/L | 41.5 | 134 | 72.2 | 114 | 71 | ND | 0 | 0 | 0 | 48
Lead | ug/L | ND | 1 | 0.387 | 0.9 | 7 | ND | 0.22 | 0.1 | 0.206 | 4
Lead_dissolved | ug/L
Magnesium | ug/L | 2580 | 42400 | 12900 | 23200 | 71 | ND | 920 | 215 | 672 | 58
Manganese | ug/L | 20 | 246 | 49.2 | 62.2 | 70 | ND | 2.33 | 0.124 | 1.05 | 38
Manganese, dissolved | ug/L | 15.2 | 80.4 | 42.6 | 57 | 62 | ND | 2.17 | 0.53 | 1.9 | 49
Mercury | ug/L | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 19
Mercury_dissolved | ug/L
Nickel | ug/L | 1.86 | 2.97 | 2.33 | 2.92 | 7 | ND | 0.56 | 0.0893 | 0.404 | 14
Nickel_dissolved | ug/L
Potassium | ug/L | 748 | 26900 | 17900 | 24000 | 71 | 590 | 3530 | 1780 | 3020 | 56
Selenium | ug/L | ND | 1.19 | 0.0464 | 0 | 70 | ND | 0 | 0 | 0 | 60
Silver | ug/L | ND | 0 | 0 | 0 | 6 | ND | 0 | 0 | 0 | 19
Silver_dissolved | ug/L
Sodium | ug/L | 3190 | 201000 | 143000 | 195000 | 5 | 7190 | 26000 | 14800 | 22000 | 16
Strontium | ug/L | 251 | 445 | 317 | 389 | 61 | 0.54 | 25.4 | 6.15 | 13.7 | 43
Thallium | ug/L | ND | 0 | 0 | 0 | 6 | ND | 0 | 0 | 0 | 18
Tin | ug/L
Tin, dissolved | ug/L
Titanium | ug/L | 2.83 | 22 | 8.46 | 18.7 | 6 | ND | 0 | 0 | 0 | 19
Vanadium | ug/L
Zinc | ug/L | 12.3 | 45.5 | 21.4 | 41.6 | 7 | 1.35 | 10.8 | 3.85 | 9.96 | 15

## PFAS
| Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
| Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit
2H,2H,3H,3H-Perfluorohexanoic Acid (3:3 FTCA) | ng/L | ND | 0 | 0 | 0 | 2
2H,2H,3H,3H-perfluorodecanoic acid (7:3 FTCA) | ng/L | ND | 0 | 0 | 0 | 2
2H,2H,3H,3H-perfluorooctanoic acid (5:3 FTCA) | ng/L | ND | 0 | 0 | 0 | 2
4,8-dioxa-3H-perfluorononanoic acid (DONA) | ng/L | ND | 0 | 0 | 0 | 2
4:2 Fluorotelomer sulfonic acid (4:2 FTSA) | ng/L | ND | 0 | 0 | 0 | 2
6:2 Fluorotelomer sulfonic acid (6:2 FTSA) | ng/L | ND | 1.76 | 0.88 | 1.67 | 2
6:2 chloropolyfluoroether sulfonic acid (6:2 CL-PFESA) | ng/L | ND | 0 | 0 | 0 | 2
6:2 fluorotelomer sulfonamide alkylbetaine (6:2 FTAB) | ng/L
8:2 Fluorotelomer sulfonic acid (8:2 FTSA) | ng/L | ND | 0 | 0 | 0 | 2
8:2 chloropolyfluoroether sulfonic acid (8:2 CL-PFESA) | ng/L | ND | 0 | 0 | 0 | 2
Hexafluoropropylene oxide dimer acid (HFPO-DA) | ng/L | ND | 0 | 0 | 0 | 2
Hexafluoropropylene oxide trimer acid (HFPO-TA) | ng/L | ND | 0 | 0 | 0 | 2
N-Ethyl perfluorooctane sulfonamide (sulfluramid) (ETFOSA) | ng/L | ND | 0 | 0 | 0 | 2
N-Ethyl perfluorooctane sulfonamidoethanol (ETFOSE) | ng/L | ND | 0 | 0 | 0 | 2
N-Methyl perfluorooctane sulfonamide (MEFOSA) | ng/L | ND | 0 | 0 | 0 | 2
N-Methyl perfluorooctane sulfonamidoethanol (MEFOSE) | ng/L | ND | 0 | 0 | 0 | 2
N-ethylperfluoro-1-octanesulfonamidoacetic acid (NETFOSAA) | ng/L | ND | 0 | 0 | 0 | 2
N-methyl perfluorooctane sulfonamido acetic acid (NMEFOSAA) | ng/L | ND | 0 | 0 | 0 | 2
Nonafluoro-3,6-dioxaheptanoic acid (NFDHA) | ng/L | ND | 0 | 0 | 0 | 2
Pentafluoropropionic anhydride (PFPA) | ng/L | ND | 8.7 | 3.77 | 7.81 | 10 | ND | 0 | 0 | 0 | 13
Perfluoro(2-ethoxyethane)sulphonic acid (PFEESA) | ng/L | ND | 0 | 0 | 0 | 2
Perfluoro-1-Octanesulfonate | ng/L | ND | 10.1 | 5.03 | 9.42 | 8
Perfluoro-1-undecanesulfonate (PFUNDS) | ng/L | ND | 0 | 0 | 0 | 2
Perfluoro-3-methoxypropanoic acid (PFMOPRA) | ng/L | ND | 0 | 0 | 0 | 2
Perfluoro-4-methoxybutanoic acid (PFMOBA) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorobutanesulfonamide (FBSA) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorobutanesulfonic acid (PFBS) | ng/L | ND | 5.2 | 1.28 | 4.92 | 10 | ND | 0 | 0 | 0 | 13
Perfluorobutanoic acid (PFBA) | ng/L | ND | 24.1 | 2.41 | 13.3 | 10 | ND | 7 | 0.877 | 5.44 | 13
Perfluorodecane sulfonic acid (PFDS) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorodecanoic acid (PFDA) | ng/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Perfluorododecanesulfonic acid (PFDOS) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorododecanoic acid (PFDOA) | ng/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Perfluoroethylcyclohexane sulfonate (PFECHS) | ng/L | ND | 0 | 0 | 0 | 2
Perfluoroheptanesulfonic acid (PFHPS) | ng/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Perfluoroheptanoic acid (PFHPA) | ng/L | ND | 6 | 1.67 | 5.37 | 10 | ND | 0 | 0 | 0 | 13
Perfluorohexanesulfonamide (FHXSA) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorohexanesulfonic acid (PFHXS) | ng/L | ND | 3.8 | 0.951 | 3.12 | 10 | ND | 0 | 0 | 0 | 13
Perfluorohexanoic acid (PFHXA) | ng/L | ND | 8.26 | 4.65 | 8.05 | 10 | ND | 0 | 0 | 0 | 13
Perfluorononanesulfonic acid (PFNS) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorononanoic acid (PFNA) | ng/L | ND | 1.46 | 0.146 | 0.803 | 10 | ND | 0 | 0 | 0 | 13
Perfluorooctadecanoic acid (PFODA) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorooctane sulfonic acid (PFOS) | ng/L | ND | 19.2 | 7.15 | 17.3 | 12 | ND | 0 | 0 | 0 | 16
Perfluorooctane sulfonic acid (PFOS, branched) | ng/L | 1.63 | 2.68 | 2.16 | 2.63 | 2 | ND | 0 | 0 | 0 | 13
Perfluorooctane sulfonic acid (PFOS, linear) | ng/L | [5 empty] | ND | 0 | 0 | 0 | 13
Perfluorooctanesulfonamide (PFOSA) | ng/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Perfluorooctanoic acid (PFOA) | ng/L | ND | 6.1 | 3.89 | 5.87 | 10 | ND | 0 | 0 | 0 | 13
Perfluoropentansulfonic acid (PFPES) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorotetradecanoic acid (PFTEA) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorotridecanoic acid (PFTRDA) | ng/L | ND | 0 | 0 | 0 | 2
Perfluoroundecanoic acid (PFUNA) | ng/L | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
perfluorohexadecanoic acid (PFHXDA) | ng/L | ND | 0 | 0 | 0 | 2
Perfluorooctanoic acid (PFOA) | ug/L

## PPCP
|  | Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
|  | Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit | Lab
1,7-dimethylxanthine | ng/L | ALS | ND | 164 | 41.8 | 144 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | 8.6 | 51 | 28.7 | 48.9 | 7 | ND | 27 | 7.12 | 23.1 | 8
Acesulfame-K | ng/L | ALS | ND | 534 | 66.8 | 347 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | ND | 1000 | 187 | 778 | 7 | ND | 60 | 16.1 | 57.9 | 7
Acetaminophen | ng/L | ALS | ND | 55.8 | 6.97 | 36.3 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | ND | 71 | 10.1 | 49.7 | 7 | ND | 90 | 25.3 | 83 | 6
Albuterol | ng/L | ALS | ND | 26.3 | 5.29 | 22.7 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | 15 | 70 | 40.9 | 66.4 | 7 | ND | 0 | 0 | 0 | 8
Amoxicillin (semi-quantitative/qualitative) | ng/L | ALS | ND | 28100 | 4180 | 19200 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | 870 | 3400 | 1870 | 3280 | 7 | ND | 0 | 0 | 0 | 8
Andorostenedione | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Atenolol | ng/L | ALS | ND | 680 | 145 | 529 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | 61 | 360 | 266 | 357 | 7 | ND | 0 | 0 | 0 | 8
Bendroflumethiazide | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Bezafibrate | ng/L | ALS | ND | 331 | 102 | 263 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | 36 | 220 | 155 | 220 | 7 | ND | 0 | 0 | 0 | 6
Butalbital | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Butylparaben | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Caffeine | ng/L | ALS | ND | 814 | 132 | 569 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 90 | 33.3 | 82.5 | 7 | ND | 89 | 21 | 71.8 | 6
Carbadox | ng/L | ALS | ND | 70.2 | 10.7 | 50.9 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 7.8 | 1.11 | 5.46 | 7 | ND | 0 | 0 | 0 | 8
Carbamazepine | ng/L | ALS | 28.1 | 618 | 379 | 610 | 8 | ND | 2.41 | 0.534 | 2.09 | 7
|  | Eurofins | 280 | 1100 | 636 | 1030 | 7 | ND | 0 | 0 | 0 | 7
Carisoprodol | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Chloramphenicol | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Cimetidine (semi-quantitative) | ng/L | ALS | ND | 61 | 24.9 | 57.5 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 1500 | 266 | 1100 | 7 | ND | 0 | 0 | 0 | 8
Codeine | ng/L | Eurofins | 240 | 240 | 240 | 240 | 1 | ND | 0 | 0 | 0 | 2
Cotinine | ng/L | ALS | ND | 12.8 | 1.6 | 8.32 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 14 | 68 | 30.6 | 57.5 | 7 | ND | 0 | 0 | 0 | 8
Dehydronifedipine | ng/L | ALS | ND | 3.18 | 0.749 | 3.05 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Diazepam | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Diclofenac | ng/L | ALS | ND | 609 | 205 | 580 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 230 | 1200 | 689 | 1090 | 7 | ND | 0 | 0 | 0 | 7
Dilantin | ng/L | ALS | ND | 78.4 | 36.2 | 76.9 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 22 | 42 | 33.6 | 41.1 | 7 | ND | 0 | 0 | 0 | 8
Diltiazem | ng/L | ALS | ND | 9570 | 1760 | 7610 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 59 | 190 | 113 | 175 | 7 | ND | 0 | 0 | 0 | 7
Epitestosterone | ng/L | Eurofins | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Erythromycin (qualitative) | ng/L | ALS | ND | 5530 | 873 | 3790 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 210 | 1200 | 493 | 996 | 7 | ND | 0 | 0 | 0 | 7
Estradiol | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Estriol | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 7
Estrone | ng/L | ALS | ND | 13.8 | 1.73 | 8.97 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 42 | 23.1 | 40.8 | 7 | ND | 0 | 0 | 0 | 8
Ethinyl estradiol-17 alpha | ng/L | ALS | ND | 1120 | 314 | 1110 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 74 | 10.6 | 51.8 | 7 | ND | 0 | 0 | 0 | 8
Ethylparaben | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Flumeqine | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 382 | 47.8 | 248 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Fluoxetine | ng/L | ALS | ND | 111 | 17.4 | 82.1 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 230 | 91.9 | 206 | 7 | ND | 15 | 3.86 | 14.1 | 7
Gemfibrozil | ng/L | ALS | ND | 38.4 | 11.2 | 34.5 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 6.6 | 0.943 | 4.62 | 7 | ND | 0 | 0 | 0 | 8
Hydrocodone | ng/L | Eurofins | 180 | 180 | 180 | 180 | 1 | ND | 0 | 0 | 0 | 2
Ibuprofen | ng/L | ALS | ND | 200 | 25 | 130 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 35 | 9.14 | 33.2 | 7 | ND | 0 | 0 | 0 | 7
Iohexol | ng/L | ALS | 2620 | 11000 | 7400 | 10800 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 2100 | 15000 | 5510 | 12100 | 7 | ND | 56 | 9.33 | 42 | 6
Iopromide | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 23 | 3.29 | 16.1 | 7 | ND | 0 | 0 | 0 | 8
Isobutylparaben | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Ketoprofen | ng/L | ALS | ND | 31.7 | 3.96 | 20.6 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 17 | 8 | 16.7 | 7 | ND | 0 | 0 | 0 | 8
Ketorolac | ng/L | ALS | ND | 12.5 | 1.75 | 8.65 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 9.1 | 1.3 | 6.37 | 7 | ND | 0 | 0 | 0 | 8
Lidocaine | ng/L | ALS | 15.3 | 204 | 102 | 194 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 58 | 170 | 93.4 | 155 | 7 | ND | 0 | 0 | 0 | 8
Lincomycin | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Lopressor | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Meclofenamic acid | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Meprobamate | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 26 | 7.36 | 20.2 | 7 | ND | 0 | 0 | 0 | 8
Metformin | ng/L | ALS | ND | 228 | 45 | 183 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 20 | 2.86 | 14 | 7 | ND | 0 | 0 | 0 | 4
Methadone | ng/L | Eurofins | 22 | 22 | 22 | 22 | 1 | ND | 0 | 0 | 0 | 1
Methylparaben | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 26 | 3.71 | 18.2 | 7 | ND | 0 | 0 | 0 | 8
Morphine | ng/L | Eurofins | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Naproxen | ng/L | ALS | ND | 131 | 47.1 | 130 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 570 | 107 | 438 | 7 | ND | 0 | 0 | 0 | 7
Nifedipin (semi-quantitative) | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Norethindrone | ng/L | Eurofins
Norethisterone | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 53 | 7.57 | 37.1 | 7 | ND | 13 | 1.86 | 9.1 | 7
Oxolinic acid | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | ND | 71 | 14.4 | 54.8 | 7 | ND | 0 | 0 | 0 | 8
Oxybenzone (semi-quantitative) | ng/L | Eurofins | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 1
Pentoxifylline | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Phenazone | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Primidone | ng/L | ALS | ND | 108 | 45.1 | 103 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 24 | 200 | 98.7 | 182 | 7 | ND | 0 | 0 | 0 | 8
Progesterone | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Propranolol | ng/L | Eurofins | 270 | 270 | 270 | 270 | 1 | ND | 0 | 0 | 0 | 1
Propylparaben | ng/L | ALS | ND | 8.08 | 1.01 | 5.25 | 8 | ND | 48 | 6.99 | 34 | 8
|  | Eurofins | ND | 9 | 3.04 | 8.43 | 7 | ND | 5.8 | 0.725 | 3.77 | 8
Quinoline | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 21 | 5.86 | 20.7 | 7 | ND | 0 | 0 | 0 | 4
Salicylic acid | ng/L | ALS | ND | 51100 | 6390 | 33200 | 8 | ND | 119000 | 14900 | 77300 | 8
|  | Eurofins | ND | 380 | 107 | 377 | 7 | ND | 550 | 184 | 526 | 8
Sucralose | ng/L | ALS | 1300 | 124000 | 41700 | 124000 | 8 | ND | 2140 | 624 | 1970 | 7
|  | Eurofins | 59000 | 150000 | 93000 | 138000 | 7 | ND | 2200 | 720 | 2110 | 7
Sulfachloropyridazine | ng/L | ALS | ND | 29.2 | 3.65 | 19 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Sulfadiazine | ng/L | ALS | ND | 215 | 81.6 | 193 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 240 | 135 | 228 | 7 | ND | 0 | 0 | 0 | 8
Sulfadimethoxine | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Sulfamerazine | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 140 | 33.6 | 126 | 7 | ND | 0 | 0 | 0 | 8
Sulfamethazine | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Sulfamethizole | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Sulfamethoxazole | ng/L | ALS | ND | 443 | 97.2 | 370 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 81 | 200 | 172 | 200 | 7 | ND | 0 | 0 | 0 | 7
Sulfathiazole | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
TCEP | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 40 | 140 | 73 | 128 | 7 | ND | 0 | 0 | 0 | 7
Testosterone | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Theobromine | ng/L | ALS | ND | 2070 | 298 | 1460 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 470 | 199 | 455 | 7 | ND | 0 | 0 | 0 | 6
Theophylline (semi-quantitative/qualitative) | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 50 | 27.7 | 46.4 | 7 | ND | 41 | 10.5 | 33.8 | 6
Triclocarban (qualitative) | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 7
Triclosan | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 27 | 3.86 | 18.9 | 7 | ND | 0 | 0 | 0 | 8
Trimethoprim | ng/L | ALS | 33.8 | 552 | 264 | 529 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 180 | 500 | 334 | 470 | 7 | ND | 0 | 0 | 0 | 7
Venlafaxine | ng/L | Eurofins | 710 | 710 | 710 | 710 | 1 | ND | 0 | 0 | 0 | 2
Warfarin | ng/L | ALS | ND | 5.4 | 0.675 | 3.51 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 11 | 5.16 | 10.3 | 7 | ND | 0 | 0 | 0 | 8
Diazepam | ug/L | ALS | ND | 0 | 0 | 0 | 1
Triclosan | ug/L | ALS

## Pesticide
|  | Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
|  | Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit | Lab
2,3,6-trichlorobenzoic acid | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 12
2,4,5-trichlorophenoxyacetic acid | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
2,4-dichlorophenoxy propanoic acid | ng/L | ALS | ND | 0 | 0 | 0 | 5 | ND | 0 | 0 | 0 | 2
2,4-dichlorophenoxyacetic acid | ng/L | ALS | ND | 100 | 9.52 | 69.4 | 17 | ND | 0 | 0 | 0 | 14
|  | Eurofins | ND | 78 | 11.1 | 54.6 | 7 | ND | 0 | 0 | 0 | 8
4-(2,4-dichlorophenoxy)butanoic acid | ng/L | ALS | ND | 0 | 0 | 0 | 10
Alachlor | ng/L | ALS | ND | 0 | 0 | 0 | 7
Aldrin | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Atrazine | ng/L | ALS | ND | 4.58 | 0.728 | 3.68 | 14 | ND | 0 | 0 | 0 | 15
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Atrazine desethyl | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Atrazine desisopropyl | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Azinphos, ethyl | ng/L | ALS | ND | 0 | 0 | 0 | 10
Azinphos, methyl | ng/L | ALS | ND | 41.8 | 4.18 | 23 | 10 | ND | 0 | 0 | 0 | 13
Azoxystrobin | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Benazolin | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 12
Bentazone | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Bixafen | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Boscalid | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Bromacil | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 15
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Bromoxynil | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Carbendazim, benomyl | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Carbetamide | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Carbophenothion | ng/L | ALS | ND | 0 | 0 | 0 | 10
Chlordane | ng/L | ALS | ND | 0 | 0 | 0 | 10
Chlordane, trans | ng/L | ALS | ND | 0 | 0 | 0 | 10
Chlorfenvinphos | ng/L | ALS | ND | 0 | 0 | 0 | 10
Chloridazon | ng/L | ALS | ND | 0 | 0 | 0 | 14 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Chlormequat | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 4
Chlorothalonil | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 12
Chlorotoluron | ng/L | ALS | ND | 0 | 0 | 0 | 17 | ND | 0 | 0 | 0 | 16
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Chloroxuron | ng/L | ALS | ND | 0 | 0 | 0 | 7
Chlorpropham | ng/L | ALS | ND | 0 | 0 | 0 | 10
Chlorpyriphos, Ethyl | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Chlorpyriphos, Methyl | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Chrysene | ng/L | ALS | ND | 0 | 0 | 0 | 8
Clofibric acid | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Clopyralid | ng/L | ALS | ND | 104 | 32.6 | 95.9 | 7 | ND | 0 | 0 | 0 | 12
Cuomaphos | ng/L | ALS | ND | 0 | 0 | 0 | 7
Cyanazine | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 13
|  | Eurofins | ND | 0 | 0 | 0 | 1
Cyhalothrin, Lamda | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Cypermethrin | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Cyproconazole | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
DACT (qualitative) | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 27 | 6.71 | 24.9 | 7 | ND | 0 | 0 | 0 | 8
DEA | ng/L | ALS | ND | 11.5 | 4.85 | 11.4 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 6.7 | 16 | 10.5 | 15.4 | 7 | ND | 0 | 0 | 0 | 8
DEET | ng/L | ALS | ND | 258 | 65.9 | 215 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 22 | 80 | 45.2 | 74.8 | 5 | ND | 50 | 16.7 | 45 | 3
DIA | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 7
DNOC (2-methyl-3,5-dinitrophenol) | ng/L | ALS | ND | 239 | 34.1 | 167 | 7
DNOC (2-methyl-4,6-dinitrophenol) | ng/L | ALS | ND | 0 | 0 | 0 | 10
Dalapon | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Delta-HCH | ng/L | ALS | ND | 0 | 0 | 0 | 7
Demeton | ng/L | ALS | ND | 0 | 0 | 0 | 10
Desmetryn | ng/L | ALS | ND | 0 | 0 | 0 | 10
Diazinon | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Dicamba | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Dichlobenil | ng/L | ALS | ND | 0 | 0 | 0 | 10
Dichlorprop | ng/L | ALS | ND | 0 | 0 | 0 | 5 | ND | 0 | 0 | 0 | 10
Dichlorvos | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Dieldrin | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Diflubenzuron | ng/L | ALS | ND | 0 | 0 | 0 | 7
Diflufenican | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Dimefuron | ng/L | ALS | ND | 0 | 0 | 0 | 7
Dimethoate | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Dinoseb | ng/L | ALS | ND | 0 | 0 | 0 | 10
Disulfoton | ng/L | ALS | ND | 0 | 0 | 0 | 10
Diuron | ng/L | ALS | ND | 223 | 51.7 | 202 | 14 | ND | 0 | 0 | 0 | 15
|  | Eurofins | 25 | 88 | 43.9 | 79 | 7 | ND | 0 | 0 | 0 | 8
Endosulfan Sulphate | ng/L | ALS | ND | 0 | 0 | 0 | 4
Endosulfan, alpha | ng/L | ALS | ND | 0 | 0 | 0 | 10
Endosulfan, beta | ng/L | ALS | ND | 0 | 0 | 0 | 10
Endrin | ng/L | ALS | ND | 0 | 0 | 0 | 10
Epoxiconazole | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Ethion (Diethion) | ng/L | ALS | ND | 0 | 0 | 0 | 7
Etridiazole | ng/L | ALS | ND | 0 | 0 | 0 | 7
Etrimfos | ng/L | ALS | ND | 0 | 0 | 0 | 7
Fenitrothion | ng/L | ALS | ND | 0 | 0 | 0 | 10
Fenoprop | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Fenpropimorph | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Fenthion | ng/L | ALS | ND | 0 | 0 | 0 | 10
Flufenacet | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Fluoroxypyr | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 12
Flusilazole | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Flutriafol | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Fluxapyroxad | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Glyphosate | ng/L | ALS | [5 empty] | ND | 16 | 2.23 | 14.2 | 13
Heptachlor | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 11
Heptachlor epoxide | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Hexachlorobenzene | ng/L | ALS | ND | 0 | 0 | 0 | 10
Hexachlorocyclohexane alpha | ng/L | ALS | ND | 0 | 0 | 0 | 10
Hexachlorocyclohexane beta | ng/L | ALS | ND | 0 | 0 | 0 | 10
Hexachlorocyclohexane, gamma | ng/L | ALS | ND | 157 | 15.7 | 86.3 | 10 | ND | 0 | 0 | 0 | 12
Ioxynil | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Isodrin | ng/L | ALS | ND | 0 | 0 | 0 | 10
Isoproturon | ng/L | ALS | ND | 0 | 0 | 0 | 14 | ND | 0 | 0 | 0 | 15
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Linuron | ng/L | ALS | ND | 0 | 0 | 0 | 17 | ND | 0 | 0 | 0 | 15
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
MCPA | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
MCPB | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Malathion | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Mecoprop | ng/L | ALS | ND | 50 | 5 | 27.5 | 10 | ND | 0 | 0 | 0 | 12
Metazachlor | ng/L | ALS | ND | 0 | 0 | 0 | 11 | ND | 0 | 0 | 0 | 15
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Metconazole | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Methabenzthiazuron | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Metolachlor | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 12 | 1.71 | 8.4 | 7 | ND | 0 | 0 | 0 | 8
Metoxuron | ng/L | ALS | ND | 0 | 0 | 0 | 7
Mevinphos | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Monolinuron | ng/L | ALS | ND | 0 | 0 | 0 | 7
Monuron | ng/L | ALS | ND | 0 | 0 | 0 | 10
Omethoate | ng/L | ALS | ND | 0 | 0 | 0 | 7
Parathion, ethyl | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
Parathion, methyl | ng/L | ALS | ND | 0 | 0 | 0 | 10
Pencycuron | ng/L | ALS | ND | 0 | 0 | 0 | 7
Pendimethalin | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Pentachlorophenol | ng/L | ALS | ND | 270 | 27 | 148 | 10 | ND | 0 | 0 | 0 | 12
Pesticides | ng/L | ALS | 0 | 50400 | 18700 | 45900 | 7 | 0 | 16 | 2.42 | 14.3 | 12
Phorate | ng/L | ALS | ND | 0 | 0 | 0 | 10
Phosalone | ng/L | ALS | ND | 0 | 0 | 0 | 7
Phosphamidon I | ng/L | ALS | ND | 0 | 0 | 0 | 7
Phosphamidon II | ng/L | ALS | ND | 0 | 0 | 0 | 7
Picloram | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Pirimephos-methyl | ng/L | ALS | ND | 0 | 0 | 0 | 10
Pirimicarb | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 12
Pirimiphos, ethyl | ng/L | ALS | ND | 0 | 0 | 0 | 10
Prometryne | ng/L | ALS | ND | 10 | 1 | 5.5 | 10 | ND | 0 | 0 | 0 | 13
Propachlor | ng/L | ALS | ND | 0 | 0 | 0 | 7
Propazine | ng/L | ALS | ND | 1.46 | 0.104 | 0.511 | 14 | ND | 0 | 0 | 0 | 15
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Propetamphos | ng/L | ALS | ND | 0 | 0 | 0 | 10
Propham | ng/L | ALS | ND | 0 | 0 | 0 | 10
Propiconazole | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Propyzamide | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
Prosulfocarb | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Quinmerac | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Quintozene | ng/L | ALS | ND | 0 | 0 | 0 | 7
Ronnel | ng/L | ALS | ND | 0 | 0 | 0 | 10
Simazine | ng/L | ALS | ND | 164 | 41.3 | 141 | 14 | ND | 0 | 0 | 0 | 15
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Spiroxamine | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Sulfometuron, methyl | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 8
Tebuconazole | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 13
Tecnazine | ng/L | ALS | ND | 0 | 0 | 0 | 10
Telodrin | ng/L | ALS | ND | 0 | 0 | 0 | 7
Terbuthylazine | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 13
Terbutryn | ng/L | ALS | ND | 11 | 1.22 | 6.6 | 9 | ND | 0 | 0 | 0 | 13
Thiabendazole | ng/L | ALS | ND | 18.8 | 6.9 | 18.8 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 9.6 | 3.3 | 8.97 | 7 | ND | 0 | 0 | 0 | 8
Total hexachlorocyclohexane | ng/L | ALS | ND | 0 | 0 | 0 | 10
Transpermethrin | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 12
Triadimefon | ng/L | ALS | ND | 0 | 0 | 0 | 7
Triallate | ng/L | ALS | ND | 17.1 | 1.71 | 9.4 | 10 | ND | 0 | 0 | 0 | 13
Triazophos | ng/L | ALS | ND | 35.4 | 3.54 | 19.5 | 10 | ND | 0 | 0 | 0 | 13
Tributylin | ng/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 7
Trichlorobenzenes | ng/L | ALS | ND | 0 | 0 | 0 | 10
Triclopyr | ng/L | ALS | ND | 167 | 23.9 | 117 | 7 | ND | 0 | 0 | 0 | 12
Trietazine | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 13
Trifluralin | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
alpha-Hexabromocyclododecane | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 2
cis-Permethrin | ng/L | ALS | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 12
o,p-DDD | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 10
o,p-DDE | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 2
o,p-DDT | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
o,p-Methoxychlor | ng/L | ALS | ND | 0 | 0 | 0 | 7
p,p-DDD | ng/L | ALS | ND | 0 | 0 | 0 | 10
p,p-DDE | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
p,p-DDT | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 12
p,p-Methoxychlor | ng/L | ALS | ND | 0 | 0 | 0 | 5
Aclonifen | ug/L | ALS
Azinphos-methyl, dissolved | ug/L | ALS
Bifenox | ug/L | ALS
Chlorfenvinphos | ug/L | ALS
Chlorpyrifos | ug/L | ALS
Cybutryne | ug/L | ALS
Cyclodiene | ug/L | ALS
Cyfluthrin | ug/L | ALS
DDT - Total WFD | ug/L | ALS
Dicofol | ug/L | ALS
Endosulfan - Total WFD | ug/L | ALS
Endrin | ug/L | ALS
Epoxyheptachlor | ug/L | ALS
HCH - Total WFD | ug/L | ALS
Heptachlor - Total WFD | ug/L | ALS
Hexachlorobenzene | ug/L | ALS
Isodrin | ug/L | ALS
Methiocarb | ug/L | ALS
Permethrin | ug/L | ALS
Polybrominated Diphenyl Ethers total | ug/L | ALS
Prochloraz | ug/L | ALS
Quinoxyfen | ug/L | ALS
Thiabendazole | ug/L | ALS

## Trace Organic
|  | Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
|  | Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit | Lab
Formaldehyde | mg/L | ALS
Total Monohydric Phenols | mg/L | ALS
1 H-Benzotriazole | ng/L | ALS | 1770 | 2830 | 2300 | 2740 | 8 | ND | 0 | 0 | 0 | 10
|  | Eurofins | 1500 | 1500 | 1500 | 1500 | 1 | ND | 30 | 15 | 28.5 | 2
1,4-dioxane | ng/L | ALS | ND | 850 | 531 | 780 | 11 | ND | 0 | 0 | 0 | 11
|  | Eurofins | 240 | 560 | 462 | 560 | 4 | ND | 0 | 0 | 0 | 3
1H-Benzotriazole-5 methyl | ng/L | ALS | 1500 | 3460 | 2110 | 3210 | 7 | ND | 0 | 0 | 0 | 9
2,3-Dichlorophenol | ng/L | ALS
2,3-Dimethylphenol | ng/L | ALS
2,4,5-Trichlorophenol | ng/L | ALS
2,4,6-Trichlorophenol | ng/L | ALS
2,4,6-Triiodophenol | ng/L | ALS
2,4-Dichlorophenol | ng/L | ALS
2,4-Dimethylphenol | ng/L | ALS
2,5-Dimethylphenol | ng/L | ALS
2,6-Dichlorophenol | ng/L | ALS
2,6-Dimethylphenol | ng/L | ALS
2-Chloro-4-Methylphenol | ng/L | ALS
2-Chlorophenol | ng/L | ALS
2-Iodophenol | ng/L | ALS
2-Methylphenol | ng/L | ALS
3,4-Dimethylphenol | ng/L | ALS
3,5-Dimethylphenol | ng/L | ALS
3-Chloro-4-Methylphenol | ng/L | ALS
3-Chlorophenol | ng/L | ALS
3-Methylphenol | ng/L | ALS
4,2 And 2,5 Chloromethylphenol | ng/L | ALS
4-Chlorophenol | ng/L | ALS
4-Iodo-2-Methylphenol | ng/L | ALS
4-Iodophenol | ng/L | ALS
4-Methylphenol | ng/L | ALS
4-nonylphenol (semi-quantitative/qualitative) | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 5
|  | Eurofins | ND | 910 | 247 | 883 | 7 | ND | 0 | 0 | 0 | 6
4-tert-octylphenol | ng/L | ALS | ND | 1370 | 320 | 1310 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | ND | 49 | 10.7 | 42.1 | 7 | ND | 0 | 0 | 0 | 6
Acenaphthene | ng/L | ALS | ND | 0 | 0 | 0 | 8
Acenaphthylene | ng/L | ALS | ND | 0 | 0 | 0 | 8
Acrylamide | ng/L | ALS | [5 empty] | ND | 34 | 4.92 | 23 | 12
Anthracene | ng/L | ALS | ND | 0 | 0 | 0 | 8
Benzo(a)anthracene | ng/L | ALS | ND | 0 | 0 | 0 | 8
Bisphenol A | ng/L | ALS | ND | 48.3 | 12.4 | 41.5 | 8 | ND | 0 | 0 | 0 | 7
|  | Eurofins | ND | 34 | 13.4 | 31.6 | 7 | ND | 29 | 4.83 | 21.8 | 6
Chloroiodomethane | ng/L | ALS
Dibenz[a,h]anthracene | ng/L | ALS | ND | 0 | 0 | 0 | 8
Dibutyltin | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 2
Fluoranthene | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
Fluorene | ng/L | ALS | ND | 0 | 0 | 0 | 8
Hexabromocyclododecane (Sum of isomers) | ng/L | ALS | ND | 4 | 1.67 | 3.7 | 3 | ND | 0 | 0 | 0 | 4
Indeno[1,2,3-cd]pyrene | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
Iodoacetamide | ng/L | ALS
Iodoacetic Acid | ng/L | ALS
Iodoacetonitrile | ng/L | ALS
Iodoform | ng/L | ALS
Metaldehyde | ng/L | ALS | ND | 0 | 0 | 0 | 10 | ND | 0 | 0 | 0 | 13
PCB - Total | ng/L | ALS
PCB Congener 101 | ng/L | ALS
PCB Congener 118 | ng/L | ALS
PCB Congener 138 | ng/L | ALS
PCB Congener 153 | ng/L | ALS
PCB Congener 180 | ng/L | ALS
PCB Congener 28 | ng/L | ALS
PCB Congener 52 | ng/L | ALS
Phenol | ng/L | ALS
TCPP | ng/L | ALS | ND | 138 | 38.9 | 137 | 7 | ND | 0 | 0 | 0 | 8
|  | Eurofins | 320 | 550 | 439 | 544 | 7 | ND | 2500 | 533 | 1980 | 6
TDCPP | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
|  | Eurofins | ND | 0 | 0 | 0 | 7 | ND | 0 | 0 | 0 | 7
Tetrabutyltin | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 2
Total phenols | ng/L | ALS | [5 empty] | 0 | 298 | 87.2 | 268 | 8
Triphenyltin | ng/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 2
p-Toluenesultonic acid | ng/L | ALS | ND | 4.47 | 1.49 | 4.02 | 3 | ND | 1.2 | 0.12 | 0.66 | 10
1,2,3,4,6,7,8-Heptachlorodibenzo-p-dioxin | pg/L | ALS
1,2,3,4,6,7,8-Heptachlorodibenzofuran | pg/L | ALS
1,2,3,4,7,8,9-Heptachlorodibenzofuran | pg/L | ALS
1,2,3,4,7,8-Hexachlorodibenzo-p-dioxin | pg/L | ALS
1,2,3,4,7,8-Hexachlorodibenzofuran | pg/L | ALS
1,2,3,6,7,8-Hexachlorodibenzo-p-dioxin | pg/L | ALS
1,2,3,6,7,8-Hexachlorodibenzofuran | pg/L | ALS
1,2,3,7,8,9-Hexachlorodibenzo-p-dioxin | pg/L | ALS
1,2,3,7,8,9-Hexachlorodibenzofuran | pg/L | ALS
1,2,3,7,8-Pentachlorodibenzo-p-dioxin | pg/L | ALS
1,2,3,7,8-Pentachlorodibenzofuran | pg/L | ALS
2,3,4,6,7,8-Hexachlorodibenzofuran | pg/L | ALS
2,3,4,7,8-Pentachlorodibenzofuran | pg/L | ALS
2,3,7,8-Tetrachlorodibenzodioxin | pg/L | ALS
2,3,7,8-Tetrachlorodibenzofuran | pg/L | ALS
Octachlorodibenzo-p-dioxin | pg/L | ALS
Octachlorodibenzofuran | pg/L | ALS
Butylbenzyl Phthalate | ug/L | ALS
Chlorinated Alkanes C10-C13 | ug/L | ALS
Di-2-ethylhexyl phthalate (DEHP) | ug/L | ALS
Dibutyl phthalate | ug/L | ALS
Diethyl Phthalate | ug/L | ALS
Dimethyl phthalate | ug/L | ALS
Dioctyl phthalate | ug/L | ALS
HBCDD - Total WFD | ug/L | ALS
Hexabromocyclodecane | ug/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 3
Nonyl Phenol (all isomers) (Nonylphenol) | ug/L | ALS | ND | 2.28 | 0.561 | 2.22 | 8 | ND | 0 | 0 | 0 | 2
Tributylphosphate | ug/L | ALS | ND | 0 | 0 | 0 | 7
Triphenyltin | ug/L | ALS
beta-Hexabromocyclododecane | ug/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 2
gamma-Hexabromocyclododecane | ug/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 2

## VOC
|  | Location Name | Peel Common WTW Treated Effluent |  |  |  |  | UVAOP effluent​
|  | Calculation | Minimum | Maximum | Average | 95th Percentile | Count | Minimum | Maximum | Average | 95th Percentile | Count
Analyte | Unit | Lab
4-bromofluorobenzene | % | ALS | 97.6 | 97.6 | 97.6 | 97.6 | 1 | 102 | 105 | 104 | 105 | 2
Dibromofluoromethane | % | ALS | 118 | 118 | 118 | 118 | 1 | 115 | 116 | 116 | 116 | 2
Toluene-D8 | % | ALS | 99.4 | 99.4 | 99.4 | 99.4 | 1 | 101 | 101 | 101 | 101 | 2
Benzo[a]pyrene | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
Benzo[b]fluoranthene | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
Benzo[ghi]perylene | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
Benzo[k]fluoranthene | ng/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 8
Hexachlorobutadiene | ng/L | ALS | ND | 0 | 0 | 0 | 11 | ND | 0 | 0 | 0 | 2
NDBA | ng/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 10
NDEA | ng/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 8
NDMA | ng/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 1.8 | 0.18 | 0.99 | 10
NDPA | ng/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 10
NMEA | ng/L | ALS | ND | 10 | 1.11 | 6 | 9 | ND | 4 | 0.4 | 2.2 | 10
NMOR | ng/L | ALS | ND | 3.5 | 0.389 | 2.1 | 9 | ND | 13.2 | 2.6 | 13 | 10
NPIP | ng/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 10
NPYR | ng/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 10
1,1,1,2-tetrachloroethane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,1,1-trichloroethane | ug/L | ALS | ND | 0 | 0 | 0 | 6 | ND | 0 | 0 | 0 | 47
1,1,2,2-tetrachloroethane | ug/L | ALS | ND | 0 | 0 | 0 | 4 | ND | 0 | 0 | 0 | 2
1,1,2-trichloroethane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,1-dichloroethane | ug/L | ALS | ND | 0 | 0 | 0 | 6 | ND | 0 | 0 | 0 | 61
1,1-dichloroethene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,1-dichloropropene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,2,3-trichlorobenzene | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 2
1,2,3-trichloropropane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,2,4-trichlorobenzene | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 2
1,2,4-trimethylbenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,2-dibromo-3-chloropropane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,2-dibromoethane | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 61
1,2-dichlorobenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,2-dichloroethane | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 61
1,2-dichloropropane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,3,5-trichlorobenzene | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 2
1,3,5-trimethylbenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,3-dichlorobenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,3-dichloropropane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
1,4-dichlorobenzene | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 9
2,2-dichloropropane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
2-chlorotoluene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
4-chlorotoluene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
4-iso-propyltoluene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
BTEX | ug/L | ALS
Benzene | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 61
Bromobenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Bromochloromethane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Bromomethane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Carbon disulfide | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Carbon tetrachloride | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 61
Chlorobenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Chloroethane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Chloromethane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Dibromomethane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Dichlorodifluoromethane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
EPH (DRO) (C10-C40) | ug/L | ALS
EPH Band C11-C12 | ug/L | ALS
EPH Band C12-C16 | ug/L | ALS
EPH Band C16-C21 | ug/L | ALS
EPH Band C21-C40 | ug/L | ALS
EPH Band C35-C39 | ug/L | ALS
Ethylbenzene | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 61
Isopropylbenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
MTBE | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 61
Naphthalene | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 2
PAH 16 Total | ug/L | ALS | ND | 0 | 0 | 0 | 3
PAH Total | ug/L | ALS
Pentachlorobenzene | ug/L | ALS | ND | 0 | 0 | 0 | 4 | ND | 0 | 0 | 0 | 12
Propylbenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Styrene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Tetra and Trichloroethene | ug/L | ALS | [5 empty] | ND | 0 | 0 | 0 | 14
Tetrachloroethene (Total) | ug/L | ALS | ND | 0 | 0 | 0 | 3 | ND | 0 | 0 | 0 | 16
Tetrachloroethylene | ug/L | ALS | ND | 0 | 0 | 0 | 6 | ND | 0 | 0 | 0 | 47
Toluene | ug/L | ALS | ND | 2.85 | 0.317 | 1.71 | 9 | ND | 0 | 0 | 0 | 60
Total PAHs 4 Constituents | ug/L | ALS | [5 empty] | 0 | 0 | 0 | 0 | 2
Total chloroethenes | ug/L | ALS | [5 empty] | 0 | 0 | 0 | 0 | 47
Trichloroethylene | ug/L | ALS | ND | 0 | 0 | 0 | 6 | ND | 0 | 0 | 0 | 47
Trichlorofluoromethane | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
Trichlororethene (Total) | ug/L | ALS | ND | 0 | 0 | 0 | 3 | ND | 0 | 0 | 0 | 16
Vinyl chloride | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 12
Xylene, meta, para | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 63
Xylene, ortho | ug/L | ALS | ND | 0 | 0 | 0 | 9 | ND | 0 | 0 | 0 | 63
Xylene, total | ug/L | ALS | ND | 0 | 0 | 0 | 8 | ND | 0 | 0 | 0 | 61
cis-1,2-dichloroethene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
cis-1,3-dichloropropene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
n-Butylbenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
sec-Butylbenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
tert-amyl methyl ether | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
tert-butylbenzene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
trans-1,2-dichloroethene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2
trans-1,3-dichloropropene | ug/L | ALS | ND | 0 | 0 | 0 | 1 | ND | 0 | 0 | 0 | 2